FACILITY-RELATED CONTROL SYSTEMS

INFORMATION ASSURANCE GUIDELINE

| DOCUMENT CONTROL |  |
| --- | --- |
| VERSION | DESCRIPTION |
| Version 1.0 – 10/31/2016 | Draft |

Contents

CHAPTER 1. INTRODUCTION	3

1.1 	PURPOSE AND SCOPE	3

1.2 	BACKGROUND	3

1.3 	APPLICABLE POLICIES, STANDARDS AND PROCEDURES	4

1.4 	ROLES AND RESPONSIBILITIES	5

1.5 	REQUIRED SUBMITTALS	5

1.6 	APPLICABLE ESTCP CS TEMPLATES	7

1.7 	GLOSSARY (PER UFC 4-010-06)	7

1.8 	REQUIREMENTS FOR SUBJECT MATTER EXPERTS	12

1.9 	CS REFERENCE ARCHITECTURE	13

1.10	TEST AND DEVELOPMENT ENVIRONMENT	13

CHAPTER 2. CS CYBERSECURITY REQUIREMENTS	15

2.1 	CS CYBERSECURITY REQUIREMENTS	15

2.2 	CS CATEGORIZATION	16

2.3 	CS CONFIGURATION MANAGEMENT	16

2.2 	CS COMMISSIONING	16

2.2 	CS CONTINUOUS MONITORING	16

CHAPTER 3. DESIGN AND CONSTRUCTION RESOURCES, DELIVERABLES AND CHECKLISTS	18

3.1 	DESIGN AND CONSTRUCTION RESOURCES	18

3.2 	TYPICAL SEQUENCE OF CS DESIGN AND CONSTRUCTION ACTIVITIES	20

CHAPTER 4. BUILDING CONTROL SYSTEMS/BUILDING AUTOMATION SYSTEMS	24

4.1 CS IA SUBMITALL REQUIREMENTS	24

4.1 CS FRONT END INTEGRATION	28

4.2 CS CABLING	29

4.3 CS WIRELESS	29

CHAPTER 1. INTRODUCTION

1.1 	PURPOSE AND SCOPE This documents defines the Information Assurance Procedures for ESTCP Control Systems projects. The intention of this document is to provide a general outline and more granular guide for the planning, design, construction, operations and commissioning of the CS following the Risk Management Framework (RMF) process outlined in UFC 04-010-06 Cybersecurity of Facility-Related Control Systems.

1.2 	BACKGROUND Department of Defense Instruction (DoDI) 8500.01, Cybersecurity, and DoDI 8510.01, Risk Management Framework (RMF) for DoD Information Technology (IT), incorporate Platform IT (PIT) into the RMF process.  PIT is a category of both IT hardware and software that is physically part of, dedicated to, or essential in real time to the mission performance of special purpose systems.  PIT is further categorized as PIT products, PIT subsystems, or PIT systems.  PIT differs from “traditional” IT in that it is integral to – and dedicated to the operation of – a specific platform.  Although the term PIT is used only by DoD, the concept of categorizing components and systems dedicated to the operation of a specific platform is not.  For example, the term “Operational Technology” (OT) is also used to refer to these systems and components.

The most common forms of Facilities-Related PIT are Control Systems (CS), which are a combination of control components (e.g., electrical, mechanical, hydraulic, or pneumatic, etc.), special purpose controlling devices, and standard IT that act together upon underlying mechanical and/or electrical equipment to achieve an objective (e.g., transport of matter or energy, maintain a secure and comfortable work environment, etc.).  All automated control systems are considered PIT.  Industrial Control Systems (ICS) are automated control systems that act upon industrial systems and processes.  ICS is used as a general term that encompasses several – but not all -- types of control systems.  These include supervisory control and data acquisition (SCADA) systems, distributed control systems (DCS) and other control systems, such as the Programmable Logic Controllers (PLCs) often found in the industrial sector and critical infrastructure.

To protect its facilities and infrastructure, DoD needs to know the type, quantity and purpose of PIT it owns and uses.  For all PIT identified, including CS, the PIT owner, in coordination with an Authorizing Official (AO), must determine whether a collection of PIT products and/or subsystems “rises to the level of” a PIT System.  In accordance with DODI 8510.01, PIT products and/or subsystems which do not rise to the level of a PIT System must undergo security assessment, but do not necessarily need to be authorized under the RMF.  However, PIT Systems undergo both security assessment and authorization by an AO.

The enterprise system used to track DoD IT, including PIT, is the Enterprise Mission Assurance Support Service (eMASS).  Both “Assess and Authorize” and “Assess-Only” CS will be entered into eMASS.  In order to standardize how EI&E-owned and -operated CS information is entered into eMASS, the DoD CS Working Group (WG) is working to incorporate new data fields and PIT capabilities into eMASS.  DoD has developed a list of common CS and a corresponding control overlay selection tool for selecting an appropriate combination of security controls in the EI&E PIT Control System Master List.  The EI&E PIT Control System Master List is maintained along with this step-by-step guide on the DoD Chief Information Officer (CIO) RMF Knowledge Service portal, where it will remain a living document.

1.3 	APPLICABLE POLICIES, STANDARDS AND PROCEDURES

- CNSSI 1253, Security Categorization And Control Selection For National Security Systems 2014

- Department of Defense Instruction 8500.01, Cybersecurity, March 2014 (available online at www.dtic.mil)

- Department of Defense Instruction 8510.01, Risk Management Framework (RMF) for DoD Information Technology (IT), March 2014 (available online at www.dtic.mil)

- Department of Defense Instruction 8140 Cyberspace Workforce Management (available online at http://www.wbdg.org/pdfs/dod_cyberworkforce.pdf)

- Department of Defense Instruction 8530 Cybersecurity Activities Support to DoD Information Network Operations March 2016 (available online at http://www.wbdg.org/pdfs/DODI_853001_2016.pdf)

- Department of Defense Industrial Control Systems Advanced Tactics, Techniques and Procedures Jan 2016 (available online at http://www.wbdg.org/pdfs/jbasics_aci_ttp_2016.pdf)

- Department of Defense Handbook for Self-Assessing Security Vulnerabilities & Risks of Industrial Control Systems on DoD Installations (available online at http://www.wbdg.org/pdfs/ics_handbook.pdf)

- Federal Information Processing Standard 200 Minimum Security Requirements for Federal Information and Information Systems

- Federal Information Processing Standard 201-2 Personal Identity Verification (PIV) of Federal Employees and Contractors

- National Institute of Standards and Technology Special Publication 800-37, Guide for Applying the Risk Management Framework to Federal Information Systems, February 2010

- National Institute of Standards and Technology Special Publication 800-53 R4 Security and Privacy Controls for Federal Information Systems and Organizations 2013

- National Institute of Standards and Technology Special Publication 800-82 R2 Guide to Industrial Control Systems (ICS) Security 2015

- National Institute of Standards and Technology Special Publication SP 800-115 Technical Guide to Information Security Testing and Assessment 2008

- Department of Veterans Affairs Mental Health Facilities Design Guide 2010

- Department of Veterans Affairs Office of Information & Technology Design Guide 2011

- Department of Veterans Affairs Telecommunications and Special Telecommunication Design Manual (TDM) 01-2016

- Unified Facility Criteria Design 4-510-01 Military Medical Facilities 2014

- UFC 3-410-01 Utility Monitoring And Control System (CS) Front End And Integration 2016 (DRAFT)

- UFC 3-410-02 Direct Digital Control For HVAC And Other Building Control Systems 2016 (DRAFT)

- UFGS 23 09 00 Instrumentation and Control for HVAC (available online at www.wbdg.org)

- UFGS 23 09 23.01 LonWorks® Direct Digital Control for HVAC and Other Building Systems (available online at www.wbdg.org)

- UFGS 23 09 23.02 BACnet Direct Digital Control for HVAC and Other Building Systems (available online at www.wbdg.org)

- UFGS 25 10 10 Utility Monitoring And Control System (CS) Front End And Integration (available online at www.wbdg.org)

- Government Accounting Office Report 15-6 Federal Facility Cybersecurity 2014

- Building Industry Consulting Service International (BICSI) Telecommunications Distribution Methods Manual (TDMM)

- National Fire Protection Association (NFPA) 101 Life Safety Code 2015

- UL 639 Intrusion Detection Standard 2007

- UL 60950-1 Information Technology Equipment - Safety - Part 1: General Requirements 2013

1.4 	ROLES AND RESPONSIBILITIES

Role: Government Stakeholders

Members: Service Design Manager, Facilities Engineering Acquisition Department (FEAD), Services Civil Engineering Representative (NAVFAC, AFCEC, USACE, DPW, etc.), Integrated Product Team (IPT).

Responsibilities: Review ESTCP CS Installation Contractor submittals, test reports, and Commissioning reports.

Role: ESTCP CS Installation Contractor

Members: Contractor responsible for the installation or modification of a CS network component.  Includes the contractor’s Control Systems Cybersecurity Specialist and Integration Specialist.

Responsibilities: Responsible for production and submittal of all project Configuration Items (CI’s), project CI inventories, and design/construction/commissioning documentation associated with the installation or modification of CS systems.

Role: ESTCP CS Engineer of Record

Members: Project mechanical engineer of record, electrical engineer of record, and control system engineer of record (if applicable)

Responsibilities: Responsible for modifying the provided UFGS and ESTCP CS Engineering Manual design templates to meet the requirements of the specific project

Role: ESTCP CS Service Agreement Contractor

Members: Contractor(s) responsible for the operation and maintenance of the installation’s CS network.

Responsibilities: Following configuration management procedures during required system modifications, security patches, and firmware upgrades.

Role: ESTCP Information Owner/Steward

Members: Installation Chief Information Officer (CIO)

Responsibilities: Responsible for maintaining the current baseline of Configuration Items, management of the CI repository, and managing and tracking the security state of information systems.

Role: Security Control Assessor (SCA)

Members: Installation Chief Information Officer (CIO)

1.5 	REQUIRED SUBMITTALS

The Contractor(s) shall develop and upload into the DoD CIO eMASS tool, if required, for an Assess Only, Interim Authority To Operate (IATO), or Authority To Operate (ATO) package, all required artifacts and supporting documentation.  The required artifacts are determined by the system security classification, system categorization, and cybersecurity controls.

For ETSCP projects, the intent is to only provide the MINIMUM documentation necessary to demonstrate the R&D objective and capability to achieve an RMF approval. In general, for a Closed Restricted Network (CRN) or Stand-Alone, it will be an Assess Only project and ONLY the System Security Plan, the IT Contingency Plan, and the CONOPS Plans are required. For projects that will connect to the DoDIN, the full RMF Asses and Authorization will typically be required for the IATO or ATO packages. The RMF package information may include but is not limited to the list below:

- System Security Plan (SSP)

- Configuration Management Plan (CMP)

- Disaster Recovery Plan (DRP)

- Continuity of Operations (COP)

- Information Technology Contingency Plan (ITCP)

- Incidence Response Plan (IRP)

- Security Assessment Report (SAR)

- Plan of Action and Milestones (POAM)

- System Architecture/Topology/Data Flow

- Configuration Validation Checklist

- Security Classification Guide

- System Configuration Guide

- Hardware Inventory List

- Software Inventory List

- Physical Security Plan

- Personnel Security Plan

- Information Assurance Vulnerability Management (IAVM) Process

- Patch Management Process, Connection Approval / System Approval documentation

- Ports, Protocols, and Services (PPS) List

- Active Directory (AD) Documentation, (if applicable)

- TBD on project specific basis: Jump-Kit Rescue CD

For projects requiring an IATO or ATO, the data representing this information may either be uploaded directly, or cut and pasted from the CSET tool or the CIO Core Authorization excel file, into the eMASS tool for each applicable control. In addition, eMASS will provide a rollup of inherited controls for each system once it has been properly identified and classified. It is recommended that the current version of the Department of Homeland Security (DHS) Cyber Security Evaluation Tool (CSET) be used as a development tool for eMASS tool artifacts.

Completion of Scan/Fix/Scan Testing and Analysis:  This work is performed before the Security Control Assessor (SCA) assesses the system(s) and provides a certification recommendation to the Authorizing Official (AO).  The Contractor shall assess (scan and perform manual checks) its own system using approved cybersecurity scanning tools.  When issues are found (High, Medium, Low Impact Levels) the Contractor shall fix those issues and rescan the system to ensure all issues have been fixed and/or properly and acceptably mitigated.  High impact level findings that cannot be fixed are to be reported to the Government immediately along with a valid reason the vulnerability cannot be fixed and a mitigation plan to fix the vulnerability in the future. The goal is for the system to have a proper cybersecurity posture before the SCA comes in to assess the system. The scan/fix/scan process should find and fix all issues before the SCA’s assessment.

Completion of Documentation to Connect to the DoDIN:  This shall be based on the services connection approval process (CAP). The ESTCP Project Team shall provide required assistance and documentation to the Government to satisfy the CAP.  Normally this entails having an approved IATO or ATO, but it may vary depending on the site.  When Penetration Vulnerability Testing (PVT) will be required to be performed on the sites network then completion of the CAP should be scheduled to occur before PVT.  When PVT is not performed then the timeline for the CAP should be at least forty-five (45) days before connecting to the sites network.

1.6 	APPLICABLE ESTCP CS TEMPLATES

- Factory Acceptance Testing Checklist

- Site Acceptance Testing Checklist

- DoD RMF Core Security Authorization Package

1.7 	GLOSSARY (PER UFC 4-010-06)

1.7.1 	ACRONYMS

Acronym	Term

ACL		Access Control List

AO		Authorizing Official

BAS		Building Automation System

BCS		Building Control System

CCTV		Closed Circuit Television

CNSSI		Committee on National Security Systems Instruction

CCI		Control Correlation Identifier

COTS		Commercial Off The Shelf

CS		Control System

DoD		Department of Defense

ESS		Electronic Security System

EMCS		Energy Monitoring and Control System

FCN		Field Control Network

FISMA		Federal Information Security Management Act

FPOC		Field Point of Connection

GFE		Government Furnished Equipment

ICS		Industrial Control System

IDS		Intrusion Detection System

ISSM		Information System Security Manager

ISSO		Information System Security Officer

IP		Internet Protocol

IT		Information Technology

MOA		Memorandum Of Agreement

MOU		Memorandum Of Understanding

NIST		National Institute of Standards and Technology

OS		Operating System

PIT 		Platform Information Technology

PKI		Public Key Infrastructure

SCADA		Supervisory Control and Data Acquisition

SO		System Owner

UCS 		Utility Control System

UFC		Unified Facilities Criteria

UFGS		Unified Facilities Guide Specification

CS 		Utility Monitoring and Control System

USACE		U.S. Army Corps of Engineers

1.7.2	DEFINITION OF TERMS

Term	Definition

Authorizing Official (CNSS Glossary) A senior (federal) official or executive with the authority to formally assume responsibility for operating an information system at an acceptable level of risk to organizational operations (including mission, functions, image, or reputation), organizational assets, individuals, other organizations, and the Nation.

Building Automation System (BAS) The system consisting of a CS Front End, connected Building Control Systems which control building electrical and mechanical systems, and user interfaces for building control supervision.  The BAS is a subsystem of the Utility Monitoring and Control System. This term is being phased out in favor of CS.

Building Control System (BCS) A system that controls building electrical and mechanical systems such as HVAC (including central plants), lighting, vertical transport systems, and irrigation systems.  Building Control Systems generally do not have a full‐featured user interface; they may have “local display panels” but typically rely on the CS front end for full user interface functionality.  BCS is a subsystem of the Utility Monitoring and Control System, and is a class of Field Control System.

Closed Circuit Television System (CCTV) An ESS that allows video assessment of alarm conditions via remote monitoring and recording of video events.  Video monitoring may also be incorporated into other systems which are not CCTV.

Control Correlation Identifier (CCI) The Control Correlation Identifier (CCI) provides a standard identifier and description for each of the singular, actionable statements that comprise a security control.

Control System (CS) A system of digital controllers, communication architecture, and user interfaces that monitor, or monitor and control, infrastructure and equipment.

Controller An electronic device – usually having internal programming logic and digital and analog input/output capability – which performs control functions.  Two primary types of controller are equipment controller and supervisory controller.

Distributed Control System This term is being phased out in preference of BCS, UCS, and/or CS.

Electronic Security System (ESS) The integrated electronic system that encompasses interior and exterior (physical) intrusion detection systems (IDS), CCTV systems for assessment of alarm conditions, access control systems, data transmission media, and alarm reporting systems for monitoring, control, and display.

Energy Monitoring Control System (EMCS) Another name for a Utility Monitoring and Control System.  See CS.

Equipment Controller (EC) A controller implementing control logic to control a piece of equipment.  Note: a controller is defined by use, and many ECs also have the capability to act as supervisory controllers (SC).  Some examples of equipment controllers are air handler controllers, protective relays, and pump controllers. Note that some devices, such as power meters or smart sensors, which only perform monitoring functions are still considered equipment controllers (despite not actually controlling anything).

Facility-Related Control System A control system which controls equipment and infrastructure that is part of a DoD building, structure, or linear structure.

Field Control System (FCS) A Building Control System, Utility Control System, Access Control System, etc. within the Facility and "downstream" of the FPOC.

Field Control Network (FCN) The network used by the Building Control System, Utility Control System, etc., within a facility "downstream" of the FPOC.  This includes IP, Ethernet, RS-485, TP/FT-10 and other network infrastructure that support control system(s) in a given facility.

Field Point of Connection (FPOC) The FPOC is the point of connection between the ICS IP network and the field control network (an IP network, a non-IP network, or both).  The hardware which provides the connection at this location is an IT device such as a switch, IP router, or firewall.

[CS, PCS, ESS, etc.] Front End The portion of the control system consisting primarily of IT equipment, such as computers and related equipment, intended to perform operational functions and run monitoring and control/engineering tool application software.  The front end does not directly control physical systems; it interacts with them only through field control systems (FCS).  The front end is a component of the [CS, ESS, etc.] infrastructure (see definition).

Impact	The effect on organizational operations, organizational assets, or individuals due to a loss of Confidentiality, Integrity, or Availability in the control system.  Impact is categorized as one of three levels:

- LOW: limited adverse effect

- MODERATE: serious adverse effect

- HIGH: severe or catastrophic adverse effect

The impact level of a system is generally written in ALL CAPS for clarity.

Incident (FIPS 200) An occurrence that actually or potentially jeopardizes the confidentiality, integrity, or availability of an information system or the information the system processes, stores, or transmits or that constitutes a violation or imminent threat of violation of security policies, security procedures, or acceptable use policies

Industrial Control System (ICS) One type of control system.  Most specifically a control system which controls an industrial (manufacturing) process.  Sometimes also used to refer to other types of control systems, particularly utility control systems such as electrical, gas, or water distribution systems.

Information Technology (IT) Any equipment or interconnected system or subsystem of equipment that is used in the automatic acquisition, storage, manipulation, management, movement, control, display, switching, interchange, transmission, or reception of data or information by the executive agency.

[CS, ESS, ...] Infrastructure The portion of a control system (such as a CS or ESS) which includes all components that are not part of a field control system.  These components include the FPOC, the Platform Enclave, and the front end (i.e. it’s architecture Levels 3, 4 and 5)

Intrusion Detection System (IDS) [Physical/ESS] A system consisting of interior and exterior sensors, surveillance devices, and associated communication subsystems that collectively detect an intrusion of a specified site, facility, or perimeter and annunciate an alarm.

Intrusion Detection System (IDS) [Cyber] A device or software application that monitors network or system activities for malicious activities or policy violations, and produces reports to management.

Mobile Code (NIST SP 800-53r4) Software programs or parts of programs obtained from remote information systems, transmitted across a network, and executed on a local information system without explicit installation or execution by the recipient.

Mobile Code Technology (NIST SP 800-53r4) Software technologies that provide the mechanisms for the production and use of mobile code (e.g. Java, JavaScript, ActiveX, VBScript)

Non-Local Maintenance (NIST SP 800-53r4) Maintenance activities conducted by individuals communicating through a network; either an external network (e.g., the Internet) or an internal network.

[CS, ESS, ...] Platform Enclave Those components of the control system that are standard IT components and can be secured in a standard manner independent of the type of control system.  These components serve only the control system and include the IP network, network management and security devices (e.g., switches, routers), software, computers and/or other devices which provide management and security of the network.

Platform IT (PIT) IT, both hardware and software, which is physically part of, dedicated to, or essential in real time to the mission performance of special purpose systems.

Remote Access (NIST SP 800-53r4) Remote access is access to organizational information systems by users (or processes acting on behalf of users) communicating through external networks (e.g., the Internet).

Risk (NIST SP 800-53r4) A measure of the extent to which an entity is threatened by a potential circumstance or event, and typically a function of: (i) the adverse impacts that would arise if the circumstance or event occurs; and (ii) the likelihood of occurrence.  Information system-related security risks are those risks that arise from the loss of confidentiality, integrity, or availability of information or information systems and reflect the potential adverse impacts to organizational operations (including mission, functions, image, or reputation), organizational assets, individuals, other organizations, and the Nation.

Risk Management (NIST SP 800-53r4) The process of managing risks to organizational operations (including mission, functions, image, reputation), organizational assets, individuals, other organizations, and the Nation, resulting from the operation of an information system, and includes: (i) the conduct of a risk assessment; (ii) the implementation of a risk mitigation strategy; and (iii) employment of techniques and procedures for the continuous monitoring of the security state of the information system.

Security Content Automation Protocol (SCAP) A method for using specific standards to enable automated vulnerability management, measurement, and policy compliance evaluation (e.g., FISMA compliance). The National Vulnerability Database (NVD) is the U.S. government content repository for SCAP.

Supervisory Control and Data Acquisition (SCADA) This term is being phased out in preference of BCS, UCS, and/or CS.

Supervisory Controller A controller that implements a combination of supervisory logic (global control or optimization strategies), scheduling, alarming, event management, trending, web services or network management.  A supervisory controller may be located between the Platform Enclave and the FCS serving as the data aggregation conduit between the FCS and the front end.  Note that this arrangement is defined by use; many supervisory controllers have the capability to also directly control equipment, and serve the role of both supervisory controller and equipment controller.

Utility Control System (UCS) A type of field control system used for control of utility systems such as electrical distribution and generation, sanitary sewer collection and treatment, water generation and pumping, etc.  Building controls are excluded from a UCS, however it is possible to have a Utility Control System and a Building Control System in the same facility, and for those systems to share components such as the FPOC. A UCS is a subsystem of a Utility Monitoring and Control System (CS) and is a class of Field Control System (FCS).

Utility Monitoring and Control System (CS) The system consisting of one or more building control systems and/or utility control systems and the associated CS Infrastructure.  In other words, it is the complete utility monitoring system – from the front end to equipment controllers.  At the highest level the CS is composed of a CS Platform Enclave and CS Front End (jointly referred to as CS Infrastructure), and connected Field Control System(s).

CS IP Network The Level 4 IP network used by the CS.

Vulnerability (NIST SP 800-53r4) Weakness in an information system, system security procedures, internal controls, or implementation that could be exploited or triggered by a threat source.

1.8 	REQUIREMENTS FOR SUBJECT MATTER EXPERTS The CS shall be designed and engineered by qualified Control System Cybersecurity, Information and Communication Technology, and System Integration specialists complying with the requirements listed below.

1.8.1 	Control Systems Cybersecurity Specialist:  The Control Systems Cybersecurity specialist shall have a minimum of five years’ experience in control system network and security design and shall maintain current certification as a Global Industrial Cyber Security Professional (GISCP) or Certified Information Systems Security Professional (CISSP). The Control Systems Cybersecurity specialist must have demonstrated knowledge and experience applying IT and OT security strategies such as the application of the NIST security controls, exploitation techniques and methods, continuous monitoring, and utility/building control systems design. The résumé of the specialist must be submitted to the ESTCP Project Manager (PM) for review and approval prior to the concept phase of the project. The qualifications of the firm for whom the specialist works must also be submitted with the résumé.

1.8.2	 Information and Communication Technology Specialist:  The Information and Communication Technology specialist shall have a minimum of five years’ experience in control system network and security design and shall maintain current certification as a Registered Communications Distribution Designer (RCDD®). The Information and Communication Technology specialist must have demonstrated knowledge and experience applying IT and OT security strategies such as the application of the NIST security controls, cable network design and installation, project management, and data center design. The résumé of the specialist must be submitted to the ESTCP Project Manager (PM) for review and approval prior to the concept phase of the project. The qualifications of the firm for whom the specialist works must also be submitted with the résumé.

1.8.3 	System Integration Specialist:  The System Integration specialist shall have a minimum of five years’ experience in control system network and shall maintain current certification as a Certified System Integrator (CSI) for the products they are integrating (Tridium, Johnson Controls, Wonderware, Schneider, Schweitzer Engineering Laboratories, Rockwell, etc.) and/or be Control System Integrators Association (CISA) Certified. The System Integrator specialist must have demonstrated knowledge and experience applying IT and OT security strategies such as the application of the NIST security controls, BAS design and installation, project management, quality assurance and commissioning. The résumé of the specialist must be submitted to the ESTCP Project Manager (PM) for review and approval prior to the concept phase of the project. The qualifications of the firm for whom the specialist works must also be submitted with the résumé.

1.9 	CS REFERENCE ARCHITECTURE The DoD CS Reference Architecture as defined in UFC 04-010-06 Cybersecurity of Facility-Related Control Systems is provided in Figure 1.

Figure 1 DoD CS Reference Architecture

1.10	TEST AND DEVELOPMENT ENVIRONMENT For new or major modernization projects, the Systems Integrator will establish a Test and Development Environment (TDE) that replicates the Production Environment to the highest degree possible starting with the Level 4 Workstations, Servers, software and with at least one of each of the Level 3-0 major components, devices, and actuators. At approximately the 50-75% construction complete, the TDE will be used to perform Factory Acceptance Testing (FAT) of the project to ensure the project has end-to-end functionality, has been properly configured using the Security Content Automation Protocol (SCAP) tool and the Security Technical Implementation Guides (STIGS), all patches (OS and CS) are installed and properly configured, and begin creating the artifacts for the draft System Security Plan.

At approximately 95-100% construction complete, the TDE will be used to conduct Site Acceptance Testing of the complete CS, and if required, Penetration testing. The SAT artifacts will be included in the final System Security Plan, FMC and Jump-Kit (if required).

The ESTCP Project Team/System Integrator will transfer the TDE to the ESTCP PM for inclusion into the Platform Enclave Operations Center.

CHAPTER 2. CS CYBERSECURITY REQUIREMENTS

2.1 	CS CYBERSECURITY REQUIREMENTS As long as DOD uses outside contractors to design, construct, and operate building control systems, it is vitally important that contractors and vendors become part of the cybersecurity solution, starting with the supply chain and ending with proper disposal of obsolete equipment. Cybersecurity of the CS begins in the planning and design phases, it is imperative that the CS design and construction teams understand the NIST RMF process and the various documents and artifacts associated with an Authorization package.

The Continuous Monitoring (CM) Strategy has been developed by the DOD using the DISA ESS tool suite for the Level 4 Operations Center servers and workstations. The ESTCP PI and support/system integrator contractors will be given guidance on the tools and applications to use for Level 3 and below components and devices. The PIT Control System Cybersecurity Lifecycle is shown in Figure 2.

Figure 2 CS Cybersecurity Lifecycle

DoD has developed the facilities RMF Enclave Boundary approach that provides Defense In Depth and which is composed of two distinct authorizations:

- Platform Enclave (provided by hosting service/agency)

- Operational Architectures (the authorization that ESTCP projects will document)

The ESTCP office will assist Project Teams to obtain PE integration and documentation to coordinate their OA RMF authorization.

2.2 	CS CATEGORIZATION

A key first Step 1 of the RMF is to categorize the CS for Confidentially, Integrity and Availability (C-I-A). The RMF KS portal EI&E webpage has the CS Master List and preliminary C-I-A values. The ESTCP office in conjunction with the PE owner and the Project Team will determine the final C-I-A values. In general, the majority of the ESTCP projects are expected to be L-L-M or M-M-H systems.

2.3 	CS CONFIGURATION MANAGEMENT A CS configuration standard shall be established to support effective and efficient monitoring of the CS.  Managing the configuration requires the following:

- Maintain baseline configurations in accordance with technical specifications for systems and security technology set forth by the PE.

- Establish and enforce security configurations for individual applications such as HVAC, Lighting, and IDS systems and products employed in facility CS systems.

- Monitor and control changes to the baseline configurations and to the constituent components of security systems (including hardware, software, firmware, and documentation) throughout the respective system lifecycle.  Configuration management can be largely accomplished through updating CS documentation received during initial project installation.

- The PE and the CIO, is responsible for tracking and maintaining the baseline configuration of the CS.

2.2 	CS COMMISSIONING CS systems, subsystems, and software programming shall undergo comprehensive Factory and Site Acceptance Testing.  The acceptance test process shall be documented using a standard testing process that is implemented and assessed by a qualified independent third party.  At a minimum, the process shall meet the following requirements:

- Demonstrate the functionality of each CS device or component.

- Demonstrate performance characteristics consistent with the manufacture’s specifications.

- Demonstrate all functionality including software programming, integration of subsystems, and automation of system functions as specified for the particular project.

- Verify that network connections, IT integration, and IT security requirements meet FIPS, NIST, and all other applicable standards.

- Verify that all life-safety integration requirements and functions meet local and national codes and ordinances.

- Demonstrate startup, recovery from failure, and operator training requirements.

2.2 	CS CONTINUOUS MONITORING For ESTCP projects that require connection to the DoDIN, the Project Team will be required to demonstrate the solution is compatible with the CS continuous monitoring Host-Based Scanning System (HBSS) and ACASS for Level 4, using active scanning and a CS passive network monitoring capability to provide end-to-end monitoring of both legacy systems and new systems that can support end-to-end active scanning. The monitoring capability will be based on a robust, multi-tier architecture that provides local, regional, and NSOC alarm monitoring, as well as remote alarm assessment, dispatch, and response.  The multi-tier structure provides multiple levels of CS event visibility that corresponds to the DoD Mission Assurance program and includes redundant primary and secondary monitoring capability within regions or in clusters.

For CRN projects, CS monitoring capability shall be analyzed on a case-by-case basis to determine suitability and cost effectiveness.  The CS SSP and ITCP shall identify overall system framework and operational procedures.

CHAPTER 3. DESIGN AND CONSTRUCTION RESOURCES, DELIVERABLES AND CHECKLISTS

3.1 	DESIGN AND CONSTRUCTION RESOURCES

The CS consultants shall comply with the CS UFC’s, UFGS, and services/agencies latest construction specifications for CS, found on the Whole Building Design Guide, and augmented by other service/agency Policies and Directives.  Additional sections shall be prepared by the designer as necessary to suit the project requirements.

The Whole Building Design Guide Cybersecurity Resource Page provides current best cybersecurity practices and references for all types of building control systems and links to several tools to support the development of the RMF IA package and documentation.

A CS MAY be a hybrid, or converged, system of traditional IT products and Operational Technologies (OT) products that must now be considered an exploit vector that can be used to penetrate into the larger DoDIN network. These hybrid systems contain or transmit Personally Identifiable Information (PII), Protected Critical Infrastructure Information (PCII), Health Insurance Portability and Accountability Act (HIPAA), or Payment Card Industry (PCI) information/data. Examples of systems that may be hybrid, or converged, systems include:

- Access control/alarm systems that use badges/PIV Cards and Active Directory for keyless entry (contain PII).

- Keyless entry/keypad systems that use Active Directory (contain PII).

- Meter data management systems that interconnect with a local utility with real time demand and response (if the meter data is determined to contain PCII).

- Patient Monitoring and Wandering Systems (contain PII, HIPAA).

- Patient Comfort Systems (contain PII, HIPPA)

- Vehicle fueling/charging stations/pumps with credit card swipe (contain PCI).

- Computerized maintenance management systems/work order systems that interconnect with control system back-end controllers and devices (if the system is determined to contain PCII or PII).

IF the CS is determined to be a Hybrid/Converged system, then the RMF package will consist of both the NIST SP 800-53R4 and NIST SP 800-82R2 Security Controls. Reference the CIO RMF KS EI&E web portal for more detailed guidance.

The following tools are available for the ESTCP Project Team, designer, construction and systems integrators to use in the creation of the Test and Development Environment (TDE) and Production CS.

3.1.1. 	Cyber Security Evaluation Tool (CSET) The DHS CSET is a useful tool that supports the CS design, construction and authorization phases of the CS lifecycle. CSET incorporates NIST, ISO, SANS, and other industry standard references. CSET includes the NIST SP 800-53 R4, NIST SP 800-82 R2, the NIST Cybersecurity Framework, and the Committee for National Security Systems Instruction (CNSSI) 1253 RMF standards and guidelines.

CSET has a plug-in (on initial install of CSET use the custom option) that connects to the National Security Agency-developed GrassMarlin (GM) passive network analysis tool. GM can be used to create an initial network architecture diagram of existing CS.  The CSET tool can be used during design and construction to develop baseline risk assessments and initial System Security Plans (SSPs).  SSPs are published as Word documents that can be copied into the CIO eMASS Information Repository tool. CSET and the CIO eMASS Information Repository tool relationship is shown in Figure 3.

Figure 3 - Relationship of CSET, Component Registry, eMASS, and DITPR

3.1.2 	GrassMarlin Passive Network Discovery Tool In support of a passive means to generate an Industrial Control System network and discover IP devices, NSA developed the GrassMarlin (GM) tool.  GrassMarlin discovers and catalogs Control System on IP-based networks. GM uses a variety of sources to generate this data, including PCAP files, router and switch configuration files, CAM tables, and live network packet captures. The tool can automatically determine the available networks and generate the network topology as well as visualize the communication between hosts.  The GrassMarlin file can be imported into the CSET tool to generate the network architecture and topology diagram and the preliminary inventory of devices and components and should be included on the Jump-Kit Rescue CD.

3.1.3 	Security Content Automation Protocol (SCAP) Tool The SCAP tool is used to configure the CS BAS hardware and software to the proper DoD and Navy configurations using the Security Technical Implementation Guides (STIGS). The CS designer, construction and systems integrators will use the SCAP tool in the Test and Development Environment to create the artifacts required for the RMF package documentation. The TDE SCAP configuration should be as close as possible to the HBSS ACAS configuration and should be included on the Jump-Kit Rescue CD (if required).

3.1.4 	Samurai Software Testing For Utilities Tool The tool was developed by EPRI along with the Smart Grid and Advanced Meter Infrastructure Penetration Guides. The guides and the tool have electrical and utility analysis, penetration, exploit and RF communications procedures and processes and should be included on the Jump-Kit Rescue CD (if required).

3.1.5 	Kali Linux Tool The tool is the state of the practice penetration and exploitation tool. The tool is used primarily for penetration testing of IT systems, but is beginning to get some OT capabilities to include Modbus and DNP3 protocols and should be included on the Jump-Kit Rescue CD (if required).

3.1.6 	Glasswire Tool The tool is a combination network, firewall, usage and alert capability for IT systems. The tool can be used in the Test and Development Environment to establish the preliminary Functional-Mission Capability Baseline and should be included on the Jump-Kit Rescue CD (if required).

3.1.7 	Belarc Advisor Tool The tool is a data gathering and analysis tool for IT systems. The tool can be used in the Test and Development Environment to establish the preliminary Functional-Mission Capability Baseline and should be included on the Jump-Kit Rescue CD (if required).

3.1.8 	MalwareBytes Tool The tool is a malware and anti-virus scanner and cleaner for IT systems. The tool can be used in the Test and Development Environment to establish the preliminary Functional-Mission Capability Baseline and should be included on the Jump-Kit Rescue CD (if required).

3.1.9 	OSForensics Tool The tool is a forensics data gathering and analysis tool for IT systems. The tool can be used in the Test and Development Environment to establish the preliminary Functional-Mission Capability Baseline and should be included on the Jump-Kit Rescue CD (if required).

3.1.10 	Mandiant Redline Tool The tool is a data gathering and analysis tool for IT systems. The tool can be used in the Test and Development Environment to establish the preliminary Functional-Mission Capability Baseline and should be included on the Jump-Kit Rescue CD (if required).

3.1.11 	Microsoft SysInternals Suite Tool This suite of tools includes data gathering and analysis tools for IT systems, applications and processes, CPU and memory usage, and Registry tools. The suite can be used in the Test and Development Environment to establish the preliminary Functional-Mission Capability Baseline and should be included on the Jump-Kit Rescue CD (if required).

3.1.12 	Host-Based Scanning System (HBSS) and Assured Compliance Assessment Solution (ACAS) Tools HBSS and ACAS are components of the DISA Endpoint Security Solutions (ESS) suite which is an integrated set of capabilities that work together to detect, deter, protect, and report on cyber threats across all DOD networks. The CS designer, construction and systems integrators will not typically have access to HBSS ACAS; ESTCP CIO and DISA typically deploy the tools to the new systems being added to the DoD network.

3.2 	TYPICAL SEQUENCE OF CS DESIGN AND CONSTRUCTION ACTIVITIES

An example sequence and duration of CS activities during design and construction is outlined in Table 1.

Table 1 Typical Sequence of CS Design and Construction Activities

| Activity / Lead | New Project | Renovation Project | Typical Duration |
| --- | --- | --- | --- |
| Presolicitation RFP Considerations | Obtain the Regional and ESTCP Platform Enclaves catogorization and categorize the CS | Obtain the Regional and ESTCP Platform Enclaves catogorization and categorize the CS | NA |
| Design - Basis of Design - Concept Design (10-15%) - Design Development (35-50%) - Pre-Final (90%) - Final (100%) Lead: A/E Documents/Models/Tools: - Construction Design Documents / Building Information Model (BIM) / CAD - CSET - GrassMarlin - Draft Baseline System Security Plan (SSP) - IT Contingency Plan and CONOPS (ITCP) | CS front end or new susbsystem back end to connect to front end Confirm/revise system categorization, define network architecture, system components, concept of operations, drawings, and specifications. At 90% design create initial SSP and baseline security risk assessment. | CS front end upgrade or subsystem modernization Confirm/revise system categorization, define network architecture, system components, concept of operations, drawings, and specifications. At 90% design create initial SSP and baseline secuirty risk assessment. | 3-6 Months |
| Construction Test and Development (T&D) and Patch Management Environments (Virtual or Physical) Lead: Construction/System Integrator Documents/Models/Tools: - VM - Kali Linux - SamuraiSTFU | Conduct CS build and patch activities without impacting the organization’s production systems (test and development environment typically provided by vendor). | Validate and verify the upgrade/modernization/ patch is ready to support the additional systems without impacting the organization’s production systems (test and development environment typically provided by vendor). | 4 – 6 weeks |
| Construction Build/Configure Servers | Build and/or configure servers to properly operate the CS solution. | Build and/or configure servers to properly operate the CS solution. | 1 – 2 weeks |
| Construction Install Supporting Software Lead: Construction/System Integrator | Install supporting software on CS servers. | Install supporting software on CS servers. | 1 – 2 weeks |
| Construction Configure Supporting Software Lead: Construction/System Integrator Documents/Models/Tools: - STIGS - SCAP - Continuous Monitoring - Kali Linux - SamuraiSTFU - Penetration Testing Scope and ROE (if required) - Jump-Kit Rescue CD | Configure CS software to meet unique needs. After the operating system is loaded, apply hardening criteria (STIGs), run Security Content Automated Protocol (SCAP)-validated tool, perform factory acceptance testing (FAT) on major system components and devices, perform initial penetration testing. | Configure CS software to meet unique needs. After the operating system is loaded, apply hardening criteria (STIGS), run Security Content Automated Protocol (SCAP)-validated tool, perform FAT on major system components and devices, perform initial penetration testing. | 1 – 2 weeks |
| Construction Implement and assess security controls Lead: construction/system integrator Documents/Models/Tools: - CSET - SSP - Security Assessment Report (SAR) - Plan of Action & Milestones (POAM) - ITCP - Incident Response Procedures (IRP) - Penetration Testing Scope and ROE (if required) - Jump-Kit Rescue CD | Conduct RMF Steps 3 and 4 by applying controls identified during the requirements and design phase, by assessing the adequacy and effectiveness of security controls, and by documenting findings in the security assessment report. Create draft approval package. | Conduct RMF Steps 3 and 4 by applying controls identified during the requirements and design phase, by assessing the adequacy and effectiveness of security controls, and by documenting findings in the security assessment report. Create draft approval package. | 12 – 20 weeks |
| Conduct testing on initial build Lead: construction/system integrator Documents/Models/Tools: - Kali Linux - SamuraiSTFU | Test CS solution in a test and development environment to ensure system errors are found, corrected before solution is deployed on network. | Test CS solution in a test and development environment to ensure system errors are found, corrected before solution is deployed on network. | 2 – 4 weeks |
| Construction - conduct pilot implementation deployment Lead: construction/system integrator Documents/Models/Tools: - Kali Linux - SamuraiSTFU - OIT IT Repository - Penetration Testing Scope and ROE (if required) - Jump-Kit Rescue CD | Pilot implementation of CS solution on a small subset of user base to evaluate solution against real-world requirements. Conduct site acceptance testing, and if required final penetration testing, and create final approval package. | Conduct site acceptance testing, and if required final penetration testing, and create final approval package. | Varies with size of deployment (number of facilities and interconnections) |
| Receive Authorization (ATO) and move to production Lead: construction/system integrator Documents/Models/Tools: - OIT IT Repository - Continuous Monitoring tools - Jump-Kit Rescue CD | Deploy the CS to full production and implement continuous monitoring. | Deploy the CS to full production and extend continuous monitoring to new systems. | NA |

CHAPTER 4. BUILDING CONTROL SYSTEMS/BUILDING AUTOMATION SYSTEMS

This chapter provides guidance and the engineering requirements to the designers, construction and systems integrators to cover the lifecycle of the CS Information Assurance (IA) process.

At contract award, all CS contractors must complete or have current DOD Information Assurance Awareness training and have a security background clearance or similar e.g. Facility Access Determination – FAD (SECNAV M-5510.30).

CS contractors cannot use non-approved laptops/ computer and external portable media storage devices on the DoD network; only CS/ UCS/ BCS/ DDC government-approved field laptop and portable media will be used for both the Test and Development Environment and the Production system.

All CS construction and building modifications must meet the requirements of the local Building Standards Code, National Fire Protection Association (NFPA) 101, and Life Safety Code such as DDC raceway penetrations of fire wall boundaries.

While no CS can be guaranteed to continue to function and operate when a determined advisory has targeted the CS, the ability to withstand cyberwar attacks, even if in a degraded state, is a key consideration, particularly for Mission Critical and Mission Essential facilities. Contractors should design, construct, and operate the CS in accordance with the USCYBERCOM Industrial Control Systems Advanced Techniques, Tactics, and Procedures 2016. Understanding how to Detect, Mitigate, and Recover from a cyberattack on the CS is vital; the Jump-Kit Rescue CD is a key deliverable that defines the Fully-Mission Capable (FMC) Baseline and is the living document that maintains the current CS configurations and operating parameters. USCYBERCOM, the Network Security Operations Center (NOSC), and the services Operations Center (OC) use the FMC to develop and manage the Continuous Monitoring strategy.

4.1 CS IA SUBMITALL REQUIREMENTS

Configure all installed hardware and software to comply with DOD cyber security requirements that will be needed for Risk Management Framework (RMF) certification in accordance with DoDI 8510.1 with all applicable DISA STIGs applied.  All documentation shall be submitted in the form of five (5) sets of CD-ROM containing native (editable) file formats. All software licenses are required to be in the name of the Department of the Navy.

Provide all necessary documentation for system RMF certification and accreditation to include all relevant artifacts for installed equipment (hardware and software). Documentation should include the following.

- Hardware and Software (both OS and Applications) STIG

- Provide ACAS (Nessus) and/or Security Content Automation Protocol (SCAP) scans of installed and configured systems to demonstrate DOD cyber security compliance.

- Identify and close/mitigate category 1 & 2 findings

- System/Mission Description/CONOPS/COOP

- Actual or intended installation platform/location(s)

- Hardware and Software lists if selected, including list of IA managed or IA enabled devices, if any

- Topology/architecture/boundary diagram that identifies major component(s) and all interconnections.

- Current life cycle status (acquisition milestone or fielded).

- Identification of the Platform IT Infrastructure (PITI) on the boundary diagram with sufficient detail for Office of Designated Approving Authority (ODAA) to determine accreditation status of PITI.

- Include Ports/Protocols/Services in accordance with DoD PPS CAL.

- Identify interfaces that cross differing security domains.

Provide all technical documentation including as built drawings, software and hardware inventory, standard operating procedures as well as cabling diagrams.

Project reports including system status, problem resolution, unresolved system problems, patch and updates Information Assurance Vulnerability Management (IAVM) compliance.

4.1.1 Security Controls Documents

The Security Controls Documents document the engineering requirements for the CS/ UCS/BCS/ DDC Hardware, Software/Firmware; the Platform Enclave and network topology; Operating System Software and multicast filtering, port configuration, status, statistics, mirroring, and security for reliability and redundancy; Field Control Systems software/firmware; and the various plans required as artifacts for the eMASS RMF ATO Package.

As part of the Design Development (35-50%) and Final (100%) design submittal, provide the following document deliverables:

System Authorization Documents

- Draft hardware list (Hardware list must include the following for each device):

  - Manufacturer,

  - Model,

  - Location,

  - Server and Workstation technical ratings (e.g. memory),

  - Serial number,

  - MAC addresses,

  - IP addresses.

- Software and Firmware List (list must include the following for each device):

  - Manufacturer

  - Version/subversion,

  - Location/device,

  - Used network ports/protocols/services.

(Both hardware and software/firmware lists should also include Common Criteria EAL status, eMASS entry number, and OS/IOS/Firmware version(s) as applicable).

- Network diagram

  - Network diagram must show equipment locations, names, models, and IP addresses on network communications schematic.

- Jump-Kit Rescue CD (if required)

  - The Rescue CD is a bootable CD with tools, rootkit detection, master boot record check, and other capabilities. A Recovery Jump-Kit contains the tools the CS team and IT team will need to restore a system to its last FMC state during Mitigation and Recovery. The Jump-Kits must be maintained and be a part of configuration management. When configuration files or new versions of operating systems or applications are updated, the Jump-Kits need to be updated as well.

Access Controls Summary

- Information on software access controls, port control, and protection.

- System user roles implemented by application and access privileges assigned by default to each role. If privileges can be added to, or removed from, a role, so specify.

- Details on system logon, including denial after three (3) invalid attempts, how to delay subsequent logons.

- Details on privileged accounts - who should have them and when are they used.

- Details on kinds of accounts, their associated privileges, which roles should have access, and so on - servers, wireless, equipment, meters.

- User ID/Password requirements and/or PKI requirements including details on shadowing, enforcement of password strength, encryption of passwords.

- Details of system library structure and what roles should be allowed what access privileges to library components.

- Details on remote (wireless) access by laptops or servers to meter and/or radio data. Auditing Controls Summary

- Details on auditing controls and auditing (creation of system audit trail for user accountability).

COOP or Disaster Preparedness Plan

- Contractor will work with government personnel to develop COOP and Disaster Preparedness Plan for the updated system (applications and hardware)

Configuration Management Plan

- The Fully-Mission Capable (FMC) Baseline Configuration, to be included on the Jump-Kit Rescue CD.

Vendor Configuration Management Plan

- Information required to test all patches and upgrades prior to deployment, including coordination as required with any test procedures run at vendor labs.

Contingency Plan

- Restoration Procedures – Guidance on restoring vendor software & hardware including guidance to help determine priority for restoration.

- Startup & Shutdown Procedures – Details of system initialization, shutdown/aborts designed to ensure secure system state.

Security Features Guide List and discussion of all security features of Vendor hardware and software.

- Document use of mobile code (e.g. scripts, such as Java) and protections in place to prevent malicious content from using associated runtime systems.

- Documented FIPS 140-2 validated cryptography (or equivalent) compliance.

Vulnerability Management Plan

- Information required to test all patches and upgrades prior to deployment, including coordination as required with any test procedures run at vendor labs.

- Security issues associated with implementation and maintenance of the application.

- Cybersecurity POC for resolution of Cybersecurity issues post accreditation.

Maintenance Plan

- Names and other required information of personnel who will be authorized to perform maintenance in accordance with maintenance agreement

Documented Statements

- Declaration that public domain software (e.g., freeware, shareware) is not used in the system.

- Information on Common Criteria or National Information Assurance Partnership (NIAP) or Federal Information Processing Standards (FIPS) evaluation status of hardware and software.

Include the following documents:

- As-built System Accreditation Documents (Security Controls documents, along with as-built drawings submittals). Follow requirements for as-built drawings submittal format, and additionally provide hardware and software lists in Microsoft Excel 2010 or .cvs format and the network diagram in editable AutoCAD 2010 format.

- Request an editable version of the NAVFAC ICS Checklist from the government, and annotate with information required by the checklist, as well as the date and name of the government representative who witnessed validation of each item. (Demonstrate to the satisfaction of the government that system components are in compliance with the NAVFAC ICS Checklist and Security Controls documentation prior to commissioning. Facilitate government testing of the system via network scans and Security Template Implementation Guide (STIG) testing, and provide support for interpreting scan and STIG test results as needed).

- Complete ICS Inventory (to include the following attributes, in tabular format):

| General Information | Location Information | Hardware Details | Operating System and Platform | Network Information (Actual Function, not potential function) | Miscellaneous |
| --- | --- | --- | --- | --- | --- |
| Activity Assigned Unique ID | Facility Name | Device Type | Embedded OS (Yes / No) | MAC Address(es) | Custodian Name |
| Barcode or Identifier | NFAID | Device Sub-Type | OS Vendor | IP Address(es) | Comments |
| Region | Commodity | Device Function | Operating System (O/S) | Upstream Device | Custodian Organization |
| Installation | Floor | Manufacturer | O/S Version | Protocols In Use | Custodian Phone |
| Special Area (Option DNAl) | Room | Product Line | Platform Vendor | Host Name |  |
|  | Location | Model # | Platform Product Line |  |  |
|  | System Type | Serial # | Platform |  |  |
|  | Functional System or Equipment Control | Remote Connectivity: (Wired / Wireless / None) | Platform Version |  |  |
|  |  | Network Type Used: (Serial / Ethernet / Both / None) |  |  |  |

For every PLC, RTU, Supervisory Controller, Building Controller, or other network-capable (whether networked or not upon delivery) control device, delivered on CD/DVD:

- Original software/firmware

- Original software/firmware hash

- SOP for application of software/firmware updates/patches

- POC or website for software/firmware updates/patches

- Count of interfaces and types of Protocols in use, per interface on Configuration file

- SOP for configuration

4.1 CS FRONT END INTEGRATION is the portion of the control system consisting primarily of IT equipment, such as computers and related equipment, intended to perform operational functions and run monitoring and control/engineering tool application software.  The front end does not directly control physical systems; it interacts with them only through field control systems (FCS).  The following UFC’s and UFGS’s provide detailed design guidance for the CS:

- UFC 3-410-01 Utility Monitoring And Control System (CS) Front End And Integration 2016 (DRAFT)

- UFC 3-410-02 Direct Digital Control For HVAC And Other Building Control Systems 2016 (DRAFT)

- UFGS 23 09 00 Instrumentation and Control for HVAC (available online at www.wbdg.org)

- UFGS 23 09 23.01 LonWorks® Direct Digital Control for HVAC and Other Building Systems (available online at www.wbdg.org)

- UFGS 23 09 23.02 BACnet Direct Digital Control for HVAC andOther Building Systems (available online at www.wbdg.org)

- UFGS 25 10 10 Utility Monitoring And Control System (CS) Front End And Integration (available online at www.wbdg.org)

NOTE: A major objective of the IA process is to obtain a Type Authorization for the CS and use Reciprocity to extend the ATO to other similar CS that will be added to the service/agency PE.

4.1.1 CS Front End System Elements and Features

- CS Compatibility:  All components of the CS shall be fully compatible and shall not require the addition of interface equipment or software upgrades to ensure a fully operational system.

- CS System Integration:  The CS shall be fully integrated with other CS subsystems and the Level 4 DMZ firewalls.

4.2 CS CABLING is the physical transport layer of the CS to include the IP, Ethernet and serial communication. Cabling can be legacy CAT-5, RS232, RS465 or can be next generation fiber Passive Optical Networks (PONs), or can be a combination of both. Refer to the Telecommunications and Network Engineering Requirements for more detailed guidance.

4.3 CS WIRELESS is currently a challenging area where ESTCP projects may provide insight into many aspects of best practices for wireless deployment and operation. Commercial wireless products are expanding rapidly to include 802.XX, HART, Bluetooth, and Zigbee and DoD will need to plan for and eventually incorporate these devices and protocols into the DoDIN or CS networks. If the ESTCP Project Team intends to use wireless products and devices, coordinate with the ESTCP PM ASAP to ensure the CIO, Spectrum Manager, and host PE will be prepared to support.